## PRINCIPAL
|  |  | PERFOMANCE TEST OF FEEDWATER TANK-TERMOPAIPA IV | [6 empty] | TEST DATE
[10 empty] | Day | Month | Year
|  |  |  | EQUIPMENT DESCRIPTION | [5 empty] | Test start time (hh:mm): |  | 9:00
|  | FWP in service: |  | Oxygen warranty , µg/l (ppb): | [5 empty] | Test duration (hh:mm): |  | 3:00 | 11
|  |  |  | Vent condenser (internal,external): | [5 empty] | Data measurement range (min): |  | 0:15
|  |  |  | N° of spray valves: | [5 empty] | Test end time (hh:mm): |  | 12:00
|  | ∆P (bar) | 0.6 | Storage volume (m3): |  |  | 103.5 |  |  | Average unit net load (MW): |  | 152
|  |  |  | T.external (°C): | 18
| Variable | KKS | Source | Units | DATA REGISTER
[5 empty] | 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45
| minWT | LCA60CF002 | P | ton/h | 459.9 | 433.4 | 433.4 | 428.9 | 436.8 | 430.7 | 453.3 | 450.1 | 448.6 | 451.6 | 413.2
| TinWT | LCA60CT041 | P | °C | 128 | 126.9 | 127.1 | 127.2 | 127 | 127.1 | 125.5 | 125.9 | 125.7 | 125.9 | 126
| PFWT | LAA10CP012 | P | bar | 8.5 | 8.19 | 8.17 | 8.18 | 8.18 | 8.22 | 8.2 | 8.21 | 8.27 | 8.22 | 8.09
| LFWT | LAA10CL001 | P | mm | 2295 | 2333 | 2306 | 2252 | 2218 | 2161 | 2167 | 2227 | 2263 | 2327 | 2313
| TFWT | LAA10CT001 | P | °C | 177.34 | 177.4 | 177.32 | 177.35 | 177.3 | 177.53 | 177.48 | 177.43 | 177.65 | 177.41 | 176.86
| PinST | LBS50CP511 | P | bar abs | 9.86 | 9.55 | 9.53 | 9.54 | 9.54 | 9.58 | 9.56 | 9.57 | 9.63 | 9.58 | 9.45
| TinST | LBS50CT511 | P | °C | 348.2 | 346.89 | 347.1 | 347.32 | 348.25 | 347.63 | 347.3 | 347.14 | 347.55 | 347.4 | 346.83
| PFWT | LAA10CP501 | P | bar | 8.5 | 8.19 | 8.17 | 8.18 | 8.18 | 8.22 | 8.2 | 8.21 | 8.27 | 8.22 | 8.09
| moWT-10 | LAB10CF002 | P | ton/h | 478.6 | 488.55 | 486.72 | 491.76 | 484.7 | 479.17 | 483.74 | 483.54 | 486.76 | 485.97 | 488.74
| ToWT-10 | LAB10CT001 | P | °C | 178 | 176.39 | 176.21 | 176.25 | 176.24 | 176.33 | 176.32 | 176.34 | 176.62 | 176.4 | 175.86
| O.D. inFWT | LCA60CQ004 | P | µg/l (ppb) | 17 | 17 | 16 | 17 | 18 | 18 | 17 | 15 | 14 | 14 | 18
| O.D. outFWT | LAB80CQ004 | P | µg/l (ppb) | 7.45 | 7.27 | 6.99 | 6.99 | 7.21 | 6.93 | 7.24 | 6.81 | 6.98 | 6.96 | 6.98
FEED WATER STREAM FROM LPH-2
|  |  |  | redondTvin | 348 | 347 | 347 | 347 | 348 | 348 | 347 | 347 | 348 | 347 | 347
EXTRACTION 3 STEAM
| LAC20AP010 |  |  |  |  | LAC10AP010
TO HP HEATERS
FWT
LAA10BB010
Calculations summary

## CÁLC-TEST
STEAM PROPERTIES FOR TEST
| 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45
T.satsteam (°C): | 183.7071 | 182.3433 | 182.2553 | 182.2993 | 182.2993 | 182.4753 | 182.3873 | 182.4313 | 182.6953 | 182.4753 | 181.9034
hsteam (kJ/kg): | 3151.3791 | 3149.8136 | 3149.8549 | 3149.8342 | 3152.0354 | 3151.9533 | 3149.793 | 3149.7724 | 3151.8508 | 3149.7518 | 3150.0198
hfg-steam (kJ/kg): | 2001.4086 | 2006.2239 | 2006.5345 | 2006.3792 | 2006.3792 | 2005.7579 | 2006.0685 | 2005.9132 | 2004.9812 | 2005.7579 | 2007.7771
WATER PROPERTIES
Inlet stream from LPH-2
| 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45
hFW-in (kJ/kg): | 547.4728 | 542.6641 | 543.5381 | 543.9751 | 543.1011 | 543.5381 | 536.5509 | 538.2968 | 537.4238 | 538.2968 | 538.7333
CpIN (kJ/kg.°C): | 4.2708 | 4.2672 | 4.2679 | 4.2682 | 4.2675 | 4.2679 | 4.2629 | 4.2641 | 4.2635 | 4.2641 | 4.2644
ρiN (kg/m3): | 947.9394 | 948.498 | 948.3961 | 948.3453 | 948.4471 | 948.3961 | 949.2149 | 949.0094 | 949.1121 | 949.0094 | 948.9581
VFIN (m3/h): | 485.1576 | 456.933 | 456.982 | 452.2614 | 460.5423 | 454.1351 | 477.5526 | 474.284 | 472.6523 | 475.8646 | 435.4249
Outlet stream to HPH-4
| 9:15 | 9:30 | 9:45 | 10:00 | 10:15 | 10:30 | 10:45 | 11:00 | 11:15 | 11:30 | 11:45
hFW-OUT (kJ/kg): | 750.255 | 742.8567 | 742.0306 | 742.2142 | 742.1683 | 742.5813 | 742.5354 | 742.6272 | 743.9125 | 742.9026 | 740.4251
ρOUT (kg/m3): | 929.5964 | 929.8951 | 929.93 | 929.9222 | 929.9242 | 929.9067 | 929.9086 | 929.9048 | 929.8509 | 929.8932 | 929.9988
VFOUT (m3/h): | 514.8471 | 525.3818 | 523.3942 | 528.8184 | 521.2253 | 515.2883 | 520.2016 | 519.9887 | 523.4818 | 522.6084 | 525.5276
PROPERTIES IN FWT
Tsat FWT (°C): | 173.3613 | 171.6563 | 171.5426 | 171.5995 | 171.5995 | 171.8261 | 171.713 | 171.7696 | 172.107 | 171.8261 | 171.0839
h2 (kJ/kg): | 750.4062 | 743.5982 | 743.1536 | 743.376 | 743.376 | 744.2639 | 743.8202 | 744.0421 | 745.37 | 744.2639 | 741.3684
h1 (kJ/kg): | 547.4728 | 542.6641 | 543.5381 | 543.9751 | 543.1011 | 543.5381 | 536.5509 | 538.2968 | 537.4238 | 538.2968 | 538.7333
THERMAL BALANCE
Heat load (kJ/min): | 1672422.878 | 1793159.1397 | 1772097.2278 | 1814788.953 | 1754732.1288 | 1741497.4004 | 1754602.089 | 1750772.9766 | 1791772.6981 | 1763415.3358 | 1862171.4234
Ww(h1-h2) (kJ/h): | 93329074.2618 | 87084828.5083 | 86513359.7866 | 85523030.9497 | 87480073.632 | 86452609.117 | 93955181.2268 | 92605994.0132 | 93284701.3683 | 93014745.5325 | 83728802.1174
Wsteam (kg/h): | 38871.3574 | 36191.6172 | 35946.8621 | 35538.9625 | 36318.9885 | 35906.8768 | 39050.8082 | 38493.9224 | 38763.9508 | 38667.7251 | 34761.6936
Wo (kg/h): | 478600 | 488550 | 486720 | 491760 | 484700 | 479170 | 483740 | 483540 | 486760 | 485970 | 488740
Time (min) | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
HEAT FLOW RATES
QINLET-steam (kJ/min): | 122498383.7012 | 113996849.3022 | 113227398.3161 | 111941841.1024 | 114478736.3722 | 113176800.2597 | 123001962.9087 | 121247094.42 | 122178189.2638 | 121793736.2864 | 109500022.23
QFW-iN (kJ/min): | 4196379.3186 | 3919843.727 | 3926156.545 | 3888515.2609 | 3953775.7168 | 3901697.3325 | 4053642.2573 | 4038122.8881 | 4018138.371 | 4051580.3072 | 3710076.7971
QFW-OUT (kJ/min): | 5984534.05 | 6048710.5669 | 6019352.5593 | 6083187.4808 | 5995482.9155 | 5930378.1312 | 5986568.0691 | 5984832.6615 | 6035114.2144 | 6017139.4791 | 6031255.8334
Qradiation (kJ/min):
Qtransf (kJ/min): | 1788154.7314 | 2128866.8399 | 2093196.0143 | 2194672.2198 | 2041707.1987 | 2028680.7987 | 1932925.8119 | 1946709.7734 | 2016975.8433 | 1965559.1719 | 2321179.0363
TTD (°C): | 5.7071 | 5.9533 | 6.0453 | 6.0493 | 6.0593 | 6.1453 | 6.0673 | 6.0913 | 6.0753 | 6.0753 | 6.0434
VH20 (m3): | 94.554 | 96.1196 | 95.0072 | 92.7824 | 91.3816 | 89.0332 | 89.2804 | 91.7524 | 93.2356 | 95.8724 | 95.2956
ρH2O (kg/m3): | 929.7159 | 929.7049 | 929.7196 | 929.7141 | 929.7233 | 929.6811 | 929.6902 | 929.6994 | 929.6593 | 929.703 | 929.8054 |  | 0
mH2O (kg): | 87908.3576 | 89362.8605 | 88330.0549 | 86261.1021 | 84959.6006 | 82772.4822 | 83003.1144 | 85302.1484 | 86677.3404 | 89132.8615 | 88606.3618
hH2O (kJ/kg): | 770.744 | 771.0276 | 770.6495 | 770.7913 | 770.555 | 771.642 | 771.4057 | 771.1693 | 772.2093 | 771.0748 | 768.4771
(mh)H2O (kJ): | 67754842.0356 | 68901228.2986 | 68071515.4383 | 66489305.7044 | 65466047.9891 | 63870723.3562 | 64029071.781 | 65782401.3351 | 66933049.8408 | 68728104.9888 | 68091961.2962
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0-10 | 2020-10-01 | 20-30 | 30-40 | 40-50 | 50-60 | 60-70 | 70-80 | 80-90 | 90-100
Time range | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
0
∆mH2O (kg): | 1454.5029 | -1032.8055 | -2068.9528 | -1301.5014 | -2187.1184 | 230.6322 | 2299.034 | 1375.1919 | 2455.5211 | -526.4996
∆EH2O (kJ): | -412.392 | -390.4304 | 293.2809 | -307.4803 | 2377.3123 | 54.5079 | 543.2986 | -1430.1714 | 2785.7857 | -1367.6901
msteam (kg): | 375314.8731 | 360692.3969 | 357429.1232 | 359289.7552 | 361129.3269 | 374788.4252 | 387723.653 | 386289.3661 | 387158.3796 | 367147.0938
Esteam (kJ): | 1182465677.3043 | 1136121263.3184 | 1125846176.0715 | 1132098595.0382 | 1138277598.6434 | 1180910795.5859 | 1221245257.9443 | 1217125015.3554 | 1219859122.8045 | 1156471409.4475 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Einlet with FW (kJ): | 40581115.2279 | 39230001.3598 | 39073359.0295 | 39211454.8886 | 39277365.2467 | 39776697.949 | 40458825.7269 | 40281306.2958 | 40348593.3912 | 38808285.5214
Eoutlet with FW (kJ): | 60166223.0845 | 60340315.631 | 60512700.2003 | 60393351.9815 | 59629305.2339 | 59584731.0019 | 59857003.6534 | 60099734.3795 | 60261268.4673 | 60241976.5624
Eacum (kJ): | 1162880569.4477 | 1115010949.0471 | 1104406834.9007 | 1110916697.9453 | 1117925658.6562 | 1161102762.5331 | 1201847080.0179 | 1197306587.2717 | 1199946447.7284 | 1135037718.4065
Etransf (kJ): | 19585107.8566 | 21110314.2712 | 21439341.1708 | 21181897.0929 | 20351939.9872 | 19808033.0529 | 19398177.9264 | 19818428.0837 | 19912675.0761 | 21433691.041
Thermal efficiency (%): | 95.08% | 94.87% | 94.81% | 94.84% | 94.94% | 95.12% | 95.26% | 95.22% | 95.22% | 94.96%
O2 removal eff (%) | 56.18% | 57.24% | 56.31% | 58.88% | 59.94% | 61.5% | 57.41% | 54.6% | 50.14% | 50.29%
RESULTS SUMMARY
|  |  | Av. thermal eff (%): |  | 95.03%
|  |  | Av.O2 eff (%): |  | 56.25%
Test Results

## DATOS VAPOR SAT
Presión | Temp.. | Volumen |  | Energía |  | Entalpía |  |  | Entropía
bares | °C | Especifico |  | Interna
|  | Liquido | Vapor | Liquido | Vapor | Liquido | Evap. | Vapor | Liquido | Vapor
|  | Sat. | Sat. | Sat. | Sat. | Sat. |  | Sat. | Sat. | Sat.
0.04 | 28.96 | 10.04 | 34800 | 121.45 | 2415.2 | 121.46 | 2432.9 | 2554.9 | .4226 | 84746
0.06 | 36.16 | 10.064 | 23739 | 151.53 | 2425 | 151.52 | 2415.6 | 2567.4 | .5210 | 83304
0.08 | 41.51 | 10.084 | 18103 | 173.87 | 2432.2 | 173.88 | 2403.1 | 2577 | .5926 | 82287
0.1 | 45.81 | 10.102 | 14674 | 191.82 | 2437.9 | 191.83 | 2392.8 | 2584.7 | .6493 | 81502
0.2 | 60.06 | 10.172 | 7649 | 251.38 | 2456.7 | 251.4 | 2358.3 | 2609.7 | .8320 | 79085
0.3 | 69.1 | 10.223 | 5229 | 289.2 | 2468.4 | 289.23 | 2336.1 | 2625.3 | .9439 | 77686
0.4 | 75.87 | 10.265 | 3993 | 317.53 | 24770 | 317.58 | 2319.2 | 2636.8 | 10259 | 76700
0.5 | 81.33 | 10.3 | 3240 | 340.44 | 2483.9 | 340.49 | 2305.4 | 2645.9 | 10910 | 75939
0.6 | 85.94 | 10.331 | 2732 | 359.79 | 2489.6 | 359.86 | 2293.6 | 2653.5 | 11453 | 75320
0.7 | 89.95 | 10.36 | 2365 | 376.63 | 2494.5 | 376.7 | 2283.3 | 2660 | 11919 | 74797
0.8 | 93.5 | 10.38 | 2087 | 391.58 | 2498.8 | 391.6 | 2274.1 | 2665.8 | 12329 | 74346
0.9 | 96.71 | 10.41 | 1869 | 405.06 | 2502.6 | 405.15 | 2265.7 | 2670.9 | 12695 | 73949
1 | 99.63 | 10.432 | 1694 | 417.63 | 2506.1 | 417.46 | 2258 | 2675.5 | 13026 | 73594
1.5 | 111.4 | 10.528 | 1159 | 466.94 | 2519.7 | 467.11 | 2226.5 | 2693.6 | 14336 | 72233
2 | 120.2 | 10.605 | 885.7 | 504.49 | 2529.5 | 504.7 | 2201.9 | 2706.7 | 15301 | 71271
2.5 | 127.4 | 10.672 | 718.7 | 535.1 | 2537.2 | 535.37 | 2181.5 | 2716.9 | 16072 | 70527
3 | 133.6 | 10.732 | 605.8 | 561.15 | 2543.6 | 561.47 | 2163.8 | 2725.3 | 16718 | 69919
3.5 | 138.9 | 10.786 | 524.3 | 583.95 | 2546.9 | 584.33 | 2148.1 | 2732.4 | 17275 | 69405
4 | 143.6 | 10.836 | 462.5 | 604.31 | 2553.6 | 604.74 | 2133.8 | 2738.6 | 17766 | 68959
4.5 | 147.9 | 10.882 | 414 | 622.25 | 2557.6 | 623.25 | 2120.7 | 2743.9 | 18207 | 68565
5 | 151.9 | 10.926 | 374.9 | 639.68 | 2561.2 | 640.23 | 2108.5 | 2748.7 | 18607 | 68212
6 | 158.9 | 11.006 | 315.7 | 669.9 | 2567.4 | 670.56 | 2086.3 | 2756.8 | 19312 | 67600
7 | 165 | 11.08 | 272.9 | 696.44 | 2572.5 | 697.22 | 2066.3 | 2763.5 | 19922 | 67080
8 | 170.4 | 11.148 | 240.4 | 720.22 | 2576.8 | 721.11 | 2048 | 2769.1 | 20462 | 66628
9 | 175.4 | 11.212 | 215 | 741.83 | 2580.5 | 742.83 | 2031.1 | 2773.9 | 20946 | 66226 | 20 | 0
10 | 179.9 | 11.273 | 194.4 | 761.68 | 2583.6 | 762.81 | 2015.3 | 2778.1 | 21387 | 65863 | 173 | 270
15 | 198.3 | 11.539 | 131.8 | 843.16 | 2594.5 | 844.84 | 1947.3 | 2792.2 | 23150 | 64448
20 | 212.4 | 11.767 | 99.63 | 906.44 | 2600.3 | 908.79 | 1890.7 | 2799.5 | 24474 | 63409
25 | 224 | 11.973 | 79.98 | 959.11 | 2603.1 | 962.11 | 1841 | 2803.1 | 25547 | 62575
30 | 233.9 | 12.165 | 66.68 | 1004.8 | 2604.1 | 1008.4 | 1795.7 | 2804.2 | 26457 | 61869
35 | 242.6 | 12.347 | 57.07 | 1045.4 | 2603.7 | 1049.8 | 1753.7 | 2803.4 | 27253 | 61253
40 | 250.4 | 12.522 | 49.78 | 1082.3 | 2602.3 | 1087.3 | 1714.1 | 2801.4 | 27964 | 60701
45 | 257.5 | 12.692 | 44.06 | 1116.2 | 2600.1 | 1121.9 | 1676.4 | 2798.3 | 28610 | 60199
50 | 264 | 12.859 | 39.44 | 1147.8 | 2597.1 | 1154.2 | 1640.1 | 2794.3 | 29202 | 59734
60 | 275.6 | 13.187 | 32.44 | 1205.4 | 2589.7 | 1213.4 | 1571 | 2784.3 | 30267 | 58892
70 | 285.9 | 13.513 | 27.37 | 1257.6 | 2580.5 | 1267 | 1505.1 | 2772.1 | 31211 | 58133
80 | 295.1 | 13.842 | 23.52 | 1305.6 | 2569.8 | 1316.6 | 1441.3 | 2758 | 32068 | 57432
90 | 303.4 | 14.178 | 20.48 | 1350.5 | 2557.8 | 1363.3 | 1378.9 | 2742.1 | 32858 | 56772
100 | 311.1 | 14.524 | 18.03 | 1393 | 2544.4 | 1407.6 | 1317.1 | 2724.7 | 33596 | 56141
110 | 318.2 | 14.886 | 15.99 | 1433.7 | 2529.8 | 1450.1 | 1255.5 | 2705.6 | 34295 | 55527
120 | 324.8 | 15.267 | 14.26 | 1473 | 2513.7 | 1491.3 | 1193.6 | 2684.9 | 34962 | 54924
130 | 330.9 | 15.671 | 12.78 | 1511.1 | 2496.1 | 1531.5 | 1130.7 | 2662.2 | 35606 | 54323
140 | 336.8 | 16.107 | 11.49 | 1548.6 | 2476.8 | 1571.1 | 1066.5 | 2637.6 | 36232 | 53717
150 | 342.2 | 16.581 | 10.34 | 1585.6 | 2455.5 | 1610.5 | 1000 | 2610.5 | 36848 | 53098
160 | 347.4 | 17.107 | 9.306 | 1622.7 | 2431.7 | 1650.1 | 930.6 | 2580.6 | 37461 | 52455
170 | 352.4 | 17.702 | 8.364 | 1656.2 | 2405.0 | 1690.3 | 856.9 | 2547.2 | 38079 | 51777

## DATOS VAP.SOBREC.
21 | 4 | 1 | Superheat Temperature | Pressure | Saturation Temperature | Specific Enthalpy of Evaporation (hfg) | Specific Enthalpy of Superheated Steam (h)
200 | MES | AÑO | °C | bar absolute | °C | kJ/kg | kJ/kg
1 | January | 2009 | 340 | 7.9 | 174.977 | 2032.13 | 3138.41
2 | February | 2010 |  | 8 | 175.451 | 2030.49 | 3138.2
3 | March | 2011 |  | 8.1 | 175.921 | 2028.86 | 3137.98
4 | April | 2012 |  | 8.2 | 176.386 | 2027.23 | 3137.77
5 | May | 2013 |  | 8.3 | 176.848 | 2025.62 | 3137.56
6 | June | 2014 |  | 8.4 | 177.305 | 2024.02 | 3137.34
7 | July | 2015 |  | 8.5 | 177.759 | 2022.43 | 3137.13
8 | August | 2016 |  | 8.6 | 178.209 | 2020.85 | 3136.92
9 | September | 2017 |  | 8.7 | 178.656 | 2019.28 | 3136.7
10 | October | 2018 |  | 8.8 | 179.099 | 2017.72 | 3136.49
11 | November | 2019 |  | 8.9 | 179.538 | 2016.17 | 3136.28
12 | December | 2020 |  | 9 | 179.974 | 2014.63 | 3136.06
13 |  | 2021 |  | 9.1 | 180.406 | 2013.09 | 3135.85
14 | 1 |  |  | 9.2 | 180.835 | 2011.57 | 3135.63
15 |  |  |  | 9.3 | 181.261 | 2010.05 | 3135.42
16 |  |  |  | 9.4 | 181.684 | 2008.55 | 3135.21
17 |  |  |  | 9.5 | 182.103 | 2007.05 | 3134.99
18 |  |  |  | 9.6 | 182.519 | 2005.56 | 3134.78
19 |  |  |  | 9.7 | 182.932 | 2004.07 | 3134.56
20 |  |  |  | 9.8 | 183.342 | 2002.6 | 3134.35
21 |  |  | 341 | 7.9 | 174.977 | 2032.13 | 3140.53
22 |  |  |  | 8 | 175.451 | 2030.49 | 3140.31
23 |  |  |  | 8.1 | 175.921 | 2028.86 | 3140.1
24 |  |  |  | 8.2 | 176.386 | 2027.23 | 3139.89
25 |  |  |  | 8.3 | 176.848 | 2025.62 | 3139.68
26 |  |  |  | 8.4 | 177.305 | 2024.02 | 3139.47
27 |  |  |  | 8.5 | 177.759 | 2022.43 | 3139.25
28 |  |  |  | 8.6 | 178.209 | 2020.85 | 3139.04
29 |  |  |  | 8.7 | 178.656 | 2019.28 | 3138.83
30 |  |  |  | 8.8 | 179.099 | 2017.72 | 3138.62 | T (°C) | m | b
31 |  |  |  | 8.9 | 179.538 | 2016.17 | 3138.4 | 340 | -2.1374 | 3155.3
|  |  |  | 9 | 179.974 | 2014.63 | 3138.19 | 341 | -2.1254 | 3157.3
|  |  |  | 9.1 | 180.406 | 2013.09 | 3137.98 | 342 | -2.1145 | 3159.3
| 1 |  |  | 9.2 | 180.835 | 2011.57 | 3137.77 | 343 | -2.1027 | 3161.4
| FWP SERVICE: |  |  | 9.3 | 181.261 | 2010.05 | 3137.55 | 344 | -2.0944 | 3163.4
| LAC10AP010 |  |  | 9.4 | 181.684 | 2008.55 | 3137.34 | 345 | -2.0821 | 3165.4
| LAC20AP010 |  |  | 9.5 | 182.103 | 2007.05 | 3137.13 | 346 | -2.0717 | 3167.5
|  |  |  | 9.6 | 182.519 | 2005.56 | 3136.91 | 347 | -2.0614 | 3169.5
|  |  |  | 9.7 | 182.932 | 2004.07 | 3136.7 | 348 | -2.0508 | 3171.6
|  |  |  | 9.8 | 183.342 | 2002.6 | 3136.49 | 349 | -2.0389 | 3173.6
|  |  | 342 | 7.9 | 174.977 | 2032.13 | 3142.64 | 350 | -2.0283 | 3175.6
|  |  |  | 8 | 175.451 | 2030.49 | 3142.43 | 351 | -2.0214 | 3177.7
|  |  |  | 8.1 | 175.921 | 2028.86 | 3142.22 | 352 | -2.0105 | 3179.7
|  |  |  | 8.2 | 176.386 | 2027.23 | 3142.01 | 353 | -1.9976 | 3181.7
|  |  |  | 8.3 | 176.848 | 2025.62 | 3141.8 | 354 | -1.9886 | 3183.8
|  |  |  | 8.4 | 177.305 | 2024.02 | 3141.59 | 355 | -1.9794 | 3185.8
|  |  |  | 8.5 | 177.759 | 2022.43 | 3141.38 | 356 | -1.9689 | 3187.8
|  |  |  | 8.6 | 178.209 | 2020.85 | 3141.17
|  |  |  | 8.7 | 178.656 | 2019.28 | 3140.96
|  |  |  | 8.8 | 179.099 | 2017.72 | 3140.74
|  |  |  | 8.9 | 179.538 | 2016.17 | 3140.53
|  |  |  | 9 | 179.974 | 2014.63 | 3140.32
|  |  |  | 9.1 | 180.406 | 2013.09 | 3140.11
|  |  |  | 9.2 | 180.835 | 2011.57 | 3139.9
|  |  |  | 9.3 | 181.261 | 2010.05 | 3139.69
|  |  |  | 9.4 | 181.684 | 2008.55 | 3139.47
|  |  |  | 9.5 | 182.103 | 2007.05 | 3139.26
|  |  |  | 9.6 | 182.519 | 2005.56 | 3139.05
|  |  |  | 9.7 | 182.932 | 2004.07 | 3138.84
|  |  |  | 9.8 | 183.342 | 2002.6 | 3138.62
|  |  | 343 | 7.9 | 174.977 | 2032.13 | 3144.76
|  |  |  | 8 | 175.451 | 2030.49 | 3144.55
|  |  |  | 8.1 | 175.921 | 2028.86 | 3144.34
|  |  |  | 8.2 | 176.386 | 2027.23 | 3144.13
|  |  |  | 8.3 | 176.848 | 2025.62 | 3143.92
|  |  |  | 8.4 | 177.305 | 2024.02 | 3143.71
|  |  |  | 8.5 | 177.759 | 2022.43 | 3143.5
|  |  |  | 8.6 | 178.209 | 2020.85 | 3143.29
|  |  |  | 8.7 | 178.656 | 2019.28 | 3143.08
|  |  |  | 8.8 | 179.099 | 2017.72 | 3142.87
|  |  |  | 8.9 | 179.538 | 2016.17 | 3142.66
|  |  |  | 9 | 179.974 | 2014.63 | 3142.45
|  |  |  | 9.1 | 180.406 | 2013.09 | 3142.24
|  |  |  | 9.2 | 180.835 | 2011.57 | 3142.03
|  |  |  | 9.3 | 181.261 | 2010.05 | 3141.82
|  |  |  | 9.4 | 181.684 | 2008.55 | 3141.61
|  |  |  | 9.5 | 182.103 | 2007.05 | 3141.4
|  |  |  | 9.6 | 182.519 | 2005.56 | 3141.19
|  |  |  | 9.7 | 182.932 | 2004.07 | 3140.97
|  |  |  | 9.8 | 183.342 | 2002.6 | 3140.76
|  |  | 344 | 7.9 | 174.977 | 2032.13 | 3146.88
|  |  |  | 8 | 175.451 | 2030.49 | 3146.67
|  |  |  | 8.1 | 175.921 | 2028.86 | 3146.46
|  |  |  | 8.2 | 176.386 | 2027.23 | 3146.25
|  |  |  | 8.3 | 176.848 | 2025.62 | 3146.04
|  |  |  | 8.4 | 177.305 | 2024.02 | 3145.84
|  |  |  | 8.5 | 177.759 | 2022.43 | 3145.63
|  |  |  | 8.6 | 178.209 | 2020.85 | 3145.42
|  |  |  | 8.7 | 178.656 | 2019.28 | 3145.21
|  |  |  | 8.8 | 179.099 | 2017.72 | 3145
|  |  |  | 8.9 | 179.538 | 2016.17 | 3144.79
|  |  |  | 9 | 179.974 | 2014.63 | 3144.58
|  |  |  | 9.1 | 180.406 | 2013.09 | 3144.37
|  |  |  | 9.2 | 180.835 | 2011.57 | 3144.16
|  |  |  | 9.3 | 181.261 | 2010.05 | 3143.95
|  |  |  | 9.4 | 181.684 | 2008.55 | 3143.74
|  |  |  | 9.5 | 182.103 | 2007.05 | 3143.53
|  |  |  | 9.6 | 182.519 | 2005.56 | 3143.32
|  |  |  | 9.7 | 182.932 | 2004.07 | 3143.11
|  |  |  | 9.8 | 183.342 | 2002.6 | 3142.9
|  |  | 345 | 7.9 | 174.977 | 2032.13 | 3149
|  |  |  | 8 | 175.451 | 2030.49 | 3148.79
|  |  |  | 8.1 | 175.921 | 2028.86 | 3148.58
|  |  |  | 8.2 | 176.386 | 2027.23 | 3148.37
|  |  |  | 8.3 | 176.848 | 2025.62 | 3148.17
|  |  |  | 8.4 | 177.305 | 2024.02 | 3147.96
|  |  |  | 8.5 | 177.759 | 2022.43 | 3147.75
|  |  |  | 8.6 | 178.209 | 2020.85 | 3147.54
|  |  |  | 8.7 | 178.656 | 2019.28 | 3147.33
|  |  |  | 8.8 | 179.099 | 2017.72 | 3147.13
|  |  |  | 8.9 | 179.538 | 2016.17 | 3146.92
|  |  |  | 9 | 179.974 | 2014.63 | 3146.71
|  |  |  | 9.1 | 180.406 | 2013.09 | 3146.5
|  |  |  | 9.2 | 180.835 | 2011.57 | 3146.29
|  |  |  | 9.3 | 181.261 | 2010.05 | 3146.08
|  |  |  | 9.4 | 181.684 | 2008.55 | 3145.88
|  |  |  | 9.5 | 182.103 | 2007.05 | 3145.67
|  |  |  | 9.6 | 182.519 | 2005.56 | 3145.46
|  |  |  | 9.7 | 182.932 | 2004.07 | 3145.25
|  |  |  | 9.8 | 183.342 | 2002.6 | 3145.04
|  |  | 346 | 7.9 | 174.977 | 2032.13 | 3151.11
|  |  |  | 8 | 175.451 | 2030.49 | 3150.91
|  |  |  | 8.1 | 175.921 | 2028.86 | 3150.7
|  |  |  | 8.2 | 176.386 | 2027.23 | 3150.49
|  |  |  | 8.3 | 176.848 | 2025.62 | 3150.29
|  |  |  | 8.4 | 177.305 | 2024.02 | 3150.08
|  |  |  | 8.5 | 177.759 | 2022.43 | 3149.87
|  |  |  | 8.6 | 178.209 | 2020.85 | 3149.67
|  |  |  | 8.7 | 178.656 | 2019.28 | 3149.46
|  |  |  | 8.8 | 179.099 | 2017.72 | 3149.25
|  |  |  | 8.9 | 179.538 | 2016.17 | 3149.05
|  |  |  | 9 | 179.974 | 2014.63 | 3148.84
|  |  |  | 9.1 | 180.406 | 2013.09 | 3148.63
|  |  |  | 9.2 | 180.835 | 2011.57 | 3148.42
|  |  |  | 9.3 | 181.261 | 2010.05 | 3148.22
|  |  |  | 9.4 | 181.684 | 2008.55 | 3148.01
|  |  |  | 9.5 | 182.103 | 2007.05 | 3147.8
|  |  |  | 9.6 | 182.519 | 2005.56 | 3147.59
|  |  |  | 9.7 | 182.932 | 2004.07 | 3147.38
|  |  |  | 9.8 | 183.342 | 2002.6 | 3147.18
|  |  | 347 | 7.9 | 174.977 | 2032.13 | 3153.23
|  |  |  | 8 | 175.451 | 2030.49 | 3153.02
|  |  |  | 8.1 | 175.921 | 2028.86 | 3152.82
|  |  |  | 8.2 | 176.386 | 2027.23 | 3152.61
|  |  |  | 8.3 | 176.848 | 2025.62 | 3152.41
|  |  |  | 8.4 | 177.305 | 2024.02 | 3152.2
|  |  |  | 8.5 | 177.759 | 2022.43 | 3152
|  |  |  | 8.6 | 178.209 | 2020.85 | 3151.79
|  |  |  | 8.7 | 178.656 | 2019.28 | 3151.59
|  |  |  | 8.8 | 179.099 | 2017.72 | 3151.38
|  |  |  | 8.9 | 179.538 | 2016.17 | 3151.17
|  |  |  | 9 | 179.974 | 2014.63 | 3150.97
|  |  |  | 9.1 | 180.406 | 2013.09 | 3150.76
|  |  |  | 9.2 | 180.835 | 2011.57 | 3150.55
|  |  |  | 9.3 | 181.261 | 2010.05 | 3150.35
|  |  |  | 9.4 | 181.684 | 2008.55 | 3150.14
|  |  |  | 9.5 | 182.103 | 2007.05 | 3149.93
|  |  |  | 9.6 | 182.519 | 2005.56 | 3149.73
|  |  |  | 9.7 | 182.932 | 2004.07 | 3149.52
|  |  |  | 9.8 | 183.342 | 2002.6 | 3149.31
|  |  | 348 | 7.9 | 174.977 | 2032.13 | 3155.35
|  |  |  | 8 | 175.451 | 2030.49 | 3155.14
|  |  |  | 8.1 | 175.921 | 2028.86 | 3154.94
|  |  |  | 8.2 | 176.386 | 2027.23 | 3154.73
|  |  |  | 8.3 | 176.848 | 2025.62 | 3154.53
|  |  |  | 8.4 | 177.305 | 2024.02 | 3154.33
|  |  |  | 8.5 | 177.759 | 2022.43 | 3154.12
|  |  |  | 8.6 | 178.209 | 2020.85 | 3153.92
|  |  |  | 8.7 | 178.656 | 2019.28 | 3153.71
|  |  |  | 8.8 | 179.099 | 2017.72 | 3153.51
|  |  |  | 8.9 | 179.538 | 2016.17 | 3153.3
|  |  |  | 9 | 179.974 | 2014.63 | 3153.1
|  |  |  | 9.1 | 180.406 | 2013.09 | 3152.89
|  |  |  | 9.2 | 180.835 | 2011.57 | 3152.69
|  |  |  | 9.3 | 181.261 | 2010.05 | 3152.48
|  |  |  | 9.4 | 181.684 | 2008.55 | 3152.27
|  |  |  | 9.5 | 182.103 | 2007.05 | 3152.07
|  |  |  | 9.6 | 182.519 | 2005.56 | 3151.86
|  |  |  | 9.7 | 182.932 | 2004.07 | 3151.66
|  |  |  | 9.8 | 183.342 | 2002.6 | 3151.45
|  |  | 349 | 7.9 | 174.977 | 2032.13 | 3157.46
|  |  |  | 8 | 175.451 | 2030.49 | 3157.26
|  |  |  | 8.1 | 175.921 | 2028.86 | 3157.06
|  |  |  | 8.2 | 176.386 | 2027.23 | 3156.85
|  |  |  | 8.3 | 176.848 | 2025.62 | 3156.65
|  |  |  | 8.4 | 177.305 | 2024.02 | 3156.45
|  |  |  | 8.5 | 177.759 | 2022.43 | 3156.24
|  |  |  | 8.6 | 178.209 | 2020.85 | 3156.04
|  |  |  | 8.7 | 178.656 | 2019.28 | 3155.84
|  |  |  | 8.8 | 179.099 | 2017.72 | 3155.63
|  |  |  | 8.9 | 179.538 | 2016.17 | 3155.43
|  |  |  | 9 | 179.974 | 2014.63 | 3155.22
|  |  |  | 9.1 | 180.406 | 2013.09 | 3155.02
|  |  |  | 9.2 | 180.835 | 2011.57 | 3154.82
|  |  |  | 9.3 | 181.261 | 2010.05 | 3154.61
|  |  |  | 9.4 | 181.684 | 2008.55 | 3154.41
|  |  |  | 9.5 | 182.103 | 2007.05 | 3154.2
|  |  |  | 9.6 | 182.519 | 2005.56 | 3154
|  |  |  | 9.7 | 182.932 | 2004.07 | 3153.79
|  |  |  | 9.8 | 183.342 | 2002.6 | 3153.59
|  |  | 350 | 7.9 | 174.977 | 2032.13 | 3159.58
|  |  |  | 8 | 175.451 | 2030.49 | 3159.38
|  |  |  | 8.1 | 175.921 | 2028.86 | 3159.18
|  |  |  | 8.2 | 176.386 | 2027.23 | 3158.97
|  |  |  | 8.3 | 176.848 | 2025.62 | 3158.77
|  |  |  | 8.4 | 177.305 | 2024.02 | 3158.57
|  |  |  | 8.5 | 177.759 | 2022.43 | 3158.37
|  |  |  | 8.6 | 178.209 | 2020.85 | 3158.16
|  |  |  | 8.7 | 178.656 | 2019.28 | 3157.96
|  |  |  | 8.8 | 179.099 | 2017.72 | 3157.76
|  |  |  | 8.9 | 179.538 | 2016.17 | 3157.56
|  |  |  | 9 | 179.974 | 2014.63 | 3157.35
|  |  |  | 9.1 | 180.406 | 2013.09 | 3157.15
|  |  |  | 9.2 | 180.835 | 2011.57 | 3156.95
|  |  |  | 9.3 | 181.261 | 2010.05 | 3156.74
|  |  |  | 9.4 | 181.684 | 2008.55 | 3156.54
|  |  |  | 9.5 | 182.103 | 2007.05 | 3156.34
|  |  |  | 9.6 | 182.519 | 2005.56 | 3156.13
|  |  |  | 9.7 | 182.932 | 2004.07 | 3155.93
|  |  |  | 9.8 | 183.342 | 2002.6 | 3155.73
|  |  | 351 | 7.9 | 174.977 | 2032.13 | 3161.7
|  |  |  | 8 | 175.451 | 2030.49 | 3161.5
|  |  |  | 8.1 | 175.921 | 2028.86 | 3161.3
|  |  |  | 8.2 | 176.386 | 2027.23 | 3161.1
|  |  |  | 8.3 | 176.848 | 2025.62 | 3160.89
|  |  |  | 8.4 | 177.305 | 2024.02 | 3160.69
|  |  |  | 8.5 | 177.759 | 2022.43 | 3160.49
|  |  |  | 8.6 | 178.209 | 2020.85 | 3160.29
|  |  |  | 8.7 | 178.656 | 2019.28 | 3160.09
|  |  |  | 8.8 | 179.099 | 2017.72 | 3159.89
|  |  |  | 8.9 | 179.538 | 2016.17 | 3159.68
|  |  |  | 9 | 179.974 | 2014.63 | 3159.48
|  |  |  | 9.1 | 180.406 | 2013.09 | 3159.28
|  |  |  | 9.2 | 180.835 | 2011.57 | 3159.08
|  |  |  | 9.3 | 181.261 | 2010.05 | 3158.87
|  |  |  | 9.4 | 181.684 | 2008.55 | 3158.67
|  |  |  | 9.5 | 182.103 | 2007.05 | 3158.47
|  |  |  | 9.6 | 182.519 | 2005.56 | 3158.27
|  |  |  | 9.7 | 182.932 | 2004.07 | 3158.06
|  |  |  | 9.8 | 183.342 | 2002.6 | 3157.86
|  |  | 352 | 7.9 | 174.977 | 2032.13 | 3163.82
|  |  |  | 8 | 175.451 | 2030.49 | 3163.62
|  |  |  | 8.1 | 175.921 | 2028.86 | 3163.42
|  |  |  | 8.2 | 176.386 | 2027.23 | 3163.22
|  |  |  | 8.3 | 176.848 | 2025.62 | 3163.01
|  |  |  | 8.4 | 177.305 | 2024.02 | 3162.81
|  |  |  | 8.5 | 177.759 | 2022.43 | 3162.61
|  |  |  | 8.6 | 178.209 | 2020.85 | 3162.41
|  |  |  | 8.7 | 178.656 | 2019.28 | 3162.21
|  |  |  | 8.8 | 179.099 | 2017.72 | 3162.01
|  |  |  | 8.9 | 179.538 | 2016.17 | 3161.81
|  |  |  | 9 | 179.974 | 2014.63 | 3161.61
|  |  |  | 9.1 | 180.406 | 2013.09 | 3161.41
|  |  |  | 9.2 | 180.835 | 2011.57 | 3161.21
|  |  |  | 9.3 | 181.261 | 2010.05 | 3161.01
|  |  |  | 9.4 | 181.684 | 2008.55 | 3160.8
|  |  |  | 9.5 | 182.103 | 2007.05 | 3160.6
|  |  |  | 9.6 | 182.519 | 2005.56 | 3160.4
|  |  |  | 9.7 | 182.932 | 2004.07 | 3160.2
|  |  |  | 9.8 | 183.342 | 2002.6 | 3160
|  |  | 353 | 7.9 | 174.977 | 2032.13 | 3165.93
|  |  |  | 8 | 175.451 | 2030.49 | 3165.73
|  |  |  | 8.1 | 175.921 | 2028.86 | 3165.53
|  |  |  | 8.2 | 176.386 | 2027.23 | 3165.34
|  |  |  | 8.3 | 176.848 | 2025.62 | 3165.14
|  |  |  | 8.4 | 177.305 | 2024.02 | 3164.94
|  |  |  | 8.5 | 177.759 | 2022.43 | 3164.74
|  |  |  | 8.6 | 178.209 | 2020.85 | 3164.54
|  |  |  | 8.7 | 178.656 | 2019.28 | 3164.34
|  |  |  | 8.8 | 179.099 | 2017.72 | 3164.14
|  |  |  | 8.9 | 179.538 | 2016.17 | 3163.94
|  |  |  | 9 | 179.974 | 2014.63 | 3163.74
|  |  |  | 9.1 | 180.406 | 2013.09 | 3163.54
|  |  |  | 9.2 | 180.835 | 2011.57 | 3163.34
|  |  |  | 9.3 | 181.261 | 2010.05 | 3163.14
|  |  |  | 9.4 | 181.684 | 2008.55 | 3162.94
|  |  |  | 9.5 | 182.103 | 2007.05 | 3162.74
|  |  |  | 9.6 | 182.519 | 2005.56 | 3162.54
|  |  |  | 9.7 | 182.932 | 2004.07 | 3162.34
|  |  |  | 9.8 | 183.342 | 2002.6 | 3162.13
|  |  | 354 | 7.9 | 174.977 | 2032.13 | 3168.05
|  |  |  | 8 | 175.451 | 2030.49 | 3167.85
|  |  |  | 8.1 | 175.921 | 2028.86 | 3167.65
|  |  |  | 8.2 | 176.386 | 2027.23 | 3167.46
|  |  |  | 8.3 | 176.848 | 2025.62 | 3167.26
|  |  |  | 8.4 | 177.305 | 2024.02 | 3167.06
|  |  |  | 8.5 | 177.759 | 2022.43 | 3166.86
|  |  |  | 8.6 | 178.209 | 2020.85 | 3166.66
|  |  |  | 8.7 | 178.656 | 2019.28 | 3166.46
|  |  |  | 8.8 | 179.099 | 2017.72 | 3166.26
|  |  |  | 8.9 | 179.538 | 2016.17 | 3166.07
|  |  |  | 9 | 179.974 | 2014.63 | 3165.87
|  |  |  | 9.1 | 180.406 | 2013.09 | 3165.67
|  |  |  | 9.2 | 180.835 | 2011.57 | 3165.47
|  |  |  | 9.3 | 181.261 | 2010.05 | 3165.27
|  |  |  | 9.4 | 181.684 | 2008.55 | 3165.07
|  |  |  | 9.5 | 182.103 | 2007.05 | 3164.87
|  |  |  | 9.6 | 182.519 | 2005.56 | 3164.67
|  |  |  | 9.7 | 182.932 | 2004.07 | 3164.47
|  |  |  | 9.8 | 183.342 | 2002.6 | 3164.27
|  |  | 355 | 7.9 | 174.977 | 2032.13 | 3170.17
|  |  |  | 8 | 175.451 | 2030.49 | 3169.97
|  |  |  | 8.1 | 175.921 | 2028.86 | 3169.77
|  |  |  | 8.2 | 176.386 | 2027.23 | 3169.58
|  |  |  | 8.3 | 176.848 | 2025.62 | 3169.38
|  |  |  | 8.4 | 177.305 | 2024.02 | 3169.18
|  |  |  | 8.5 | 177.759 | 2022.43 | 3168.98
|  |  |  | 8.6 | 178.209 | 2020.85 | 3168.79
|  |  |  | 8.7 | 178.656 | 2019.28 | 3168.59
|  |  |  | 8.8 | 179.099 | 2017.72 | 3168.39
|  |  |  | 8.9 | 179.538 | 2016.17 | 3168.19
|  |  |  | 9 | 179.974 | 2014.63 | 3167.99
|  |  |  | 9.1 | 180.406 | 2013.09 | 3167.8
|  |  |  | 9.2 | 180.835 | 2011.57 | 3167.6
|  |  |  | 9.3 | 181.261 | 2010.05 | 3167.4
|  |  |  | 9.4 | 181.684 | 2008.55 | 3167.2
|  |  |  | 9.5 | 182.103 | 2007.05 | 3167
|  |  |  | 9.6 | 182.519 | 2005.56 | 3166.8
|  |  |  | 9.7 | 182.932 | 2004.07 | 3166.61
|  |  |  | 9.8 | 183.342 | 2002.6 | 3166.41
|  |  | 356 | 7.9 | 174.977 | 2032.13 | 3172.28
|  |  |  | 8 | 175.451 | 2030.49 | 3172.09
|  |  |  | 8.1 | 175.921 | 2028.86 | 3171.89
|  |  |  | 8.2 | 176.386 | 2027.23 | 3171.7
|  |  |  | 8.3 | 176.848 | 2025.62 | 3171.5
|  |  |  | 8.4 | 177.305 | 2024.02 | 3171.3
|  |  |  | 8.5 | 177.759 | 2022.43 | 3171.11
|  |  |  | 8.6 | 178.209 | 2020.85 | 3170.91
|  |  |  | 8.7 | 178.656 | 2019.28 | 3170.71
|  |  |  | 8.8 | 179.099 | 2017.72 | 3170.52
|  |  |  | 8.9 | 179.538 | 2016.17 | 3170.32
|  |  |  | 9 | 179.974 | 2014.63 | 3170.12
|  |  |  | 9.1 | 180.406 | 2013.09 | 3169.93
|  |  |  | 9.2 | 180.835 | 2011.57 | 3169.73
|  |  |  | 9.3 | 181.261 | 2010.05 | 3169.53
|  |  |  | 9.4 | 181.684 | 2008.55 | 3169.33
|  |  |  | 9.5 | 182.103 | 2007.05 | 3169.14
|  |  |  | 9.6 | 182.519 | 2005.56 | 3168.94
|  |  |  | 9.7 | 182.932 | 2004.07 | 3168.74
|  |  |  | 9.8 | 183.342 | 2002.6 | 3168.54

## ANÁLISIS CONTINUO
Suponiendo proceso adiabático (Qtransf=0):
y = fracción de vapor de turbina hacia extracción
Factor y | 0.077876 | 0.076786 | 0.076158 | 0.076074 | 0.076302 | 0.076308 | 0.078823 | 0.078243 | 0.07898 | 0.078349 | 0.077238
HL (kJ/h) | 93259515.384 | 86763464.1547 | 86026687.0844 | 85024749.3638 | 86952570.3621 | 85727931.6685 | 93372770.5228 | 91969132.6013 | 92630849.2575 | 92399988.5017 | 83339032.1908
TTD (°C) | 5.7071 | 5.9533 | 6.0453 | 6.0493 | 6.0593 | 6.1453 | 6.0673 | 6.0913 | 6.0753 | 6.0753 | 6.0434
msteam (ton/h) | 38.8399 | 36.047 | 35.728 | 35.3149 | 36.0819 | 35.581 | 38.788 | 38.2067 | 38.4689 | 38.3904 | 34.5863
% eficiencia | 91.74% | 89.56% | 89.73% | 89.11% | 90.07% | 89.99% | 90.98% | 90.84% | 90.5% | 90.78% | 88.09%